CS July 2003 JULY_FIRESTOPPING.doc 3559 words, 0 pics

Ending the “He Who Pokes It, Fills It” Mentality

Firestopping for the 21st Century

by Bill McHugh

In the past few years, many industry leading programs have been successfully introduced and are beginning to take hold in the firestopping industry. New developments in testing and contractor quality programs are helping improve passive fire and life safety while providing innovation to the firestop contracting industry.

Firestop systems have been qualified for use by testing protocol such as ASTM International E 814, Standard Test Method for Fire Tests of Through-Penetration Fire Stops, and Underwriters Laboratories (UL) 1479, Standard for Fire Tests of Through-Penetration Firestops. Various hybrids of the basic firestop qualification test have evolved to meet the demands of different, possibly higher movement conditions in top-of-wall, expansion joints, and perimeter wall-floor slab gaps. Each test method, however, has one thing in common: each solution is tested under the same basic protocol as UL 1479/ASTM E 814.

A new development in the firestopping industry is the ‘L’ rating. Describing air movement through firestops at ambient temperature and 204 C (400 F), L ratings establishing a firestop’s suitability in fire- and smoke-rated assemblies. The test protocol measures the amount of air traveling through a firestop system in cubic feet/minute, per square foot of opening area. UL started testing for smoke in the early 1990s, and publish L ratings in their Fire Resistance Directory, along with ‘F’ ratings (flame penetrating to the unexposed side of the assembly) and ‘T’ ratings (temperature rise on the non-fire side of the assembly, on the penetrating item, 121 C [250 F] over ambient temperatures).

L ratings can be an important part of the total life safety package, when firestopping is used in a fire resistance-rated assembly possessing both fire and smoke requirements. Model codes have various requirements for smoke passage (depending on occupancy), and while not frequently specified at this time, it is important to know and understand L ratings, as their use is on the rise. Where smoke-rated construction is required, architect/engineers (A/Es) or code/fire officials may require an L-rated firestop system.

The 2003 UL Fire Resistance Directory has a significant number of tested systems with L ratings, but not all are automatically L rated—the test is run at the option of the manufacturer sponsoring the testing. Some firestop systems have yet to be tested and L rated. Currently, UL 1479 is the only test method offering air leakage testing with L ratings, but ASTM E 814 will soon incorporate them.

Additionally, there is a relatively new test method for the building perimeter joint—the exterior skin (possibly non-fire rated construction) of a building where it meets the interior floor slab (usually fire-rated construction). The intermediate scale, multi-story test apparatus is used to fire test the slot between the perimeter wall and interior floor slab.

The firestopping market has experienced some interesting dynamics over the past few years. First, according to best estimates, the firestop products market nationally is around $220–270 million in product sales, including mineral wool packing materials used under firestop sealants, and many accessories. Growth rates, once as large as 30 percent per year, have been slowing as market-size increases become mathematically more difficult to achieve due to a larger base of business.

Second, code changes in both the International Building Code (IBC) and NFPA 5000, Building Construction and Safety Code, de-emphasizing compartmentation have been recently implemented in new projects. Reduced compartmentation means less need for firestopping, fire doors, fire dampers, and other passive fire and life safety items. The firestop market size growth seems to be normalizing at somewhere around eight percent to 15 percent per year, which is more like a normal growth business. Third, the contracting portion of firestopping, when a conservative 50/50 average of material to labor is used, is estimated at $250 million nationwide. According to contractors across the United States and Canada, more owners and general contractors are awarding firestop installation contracts to a single, specialty firestop contractor instead of the old “he who pokes it, fills it,” method which typically results in more than eight trades installing firestopping.

Contractors performing firestopping work come from various building trades. At the Firestop Contractors International Association (FCIA), an association of specialty firestopping contractors, members hail from mechanical, curtain wall, building insulation, or caulking trades, and from other trades who recognized an opportunity firestopping. FCIA has even seen members originate from trades like roofing and concrete coring.

Firestopping is a highly technical segment of the construction industry, where a zero tolerance attitude is required to get the job done. “Firestopping is not a tolerances trade,” says Don Sabrsula of Firesafe of Houston Inc., a firestopping and mechanical insulation contractor. “When a firm intentionally or unintentionally misapplies firestopping materials, or varies from the tested and listed system design, the system may not work and put life safety and property protection in jeopardy.

IMICO Inc.’s Alec Rexroat, who is also the executive director of the Illinois Regional Insulation Contractors Association, seconds Sabrsula’s statement: “It took a lot of convincing for field crews to understand this zero tolerance mentality. Until they understood the program, we did not let them apply firestop products.” He explains these tradespersons have been working within construction tolerances for most of their careers, but “Once they understood firestopping protocol is different, operations became easier to control.”

When a variance to the tested system was encountered, Rexroat’s crews knew to find another tested system in their documentation, or get an engineering judgment through the office from the manufacturer’s fire protection engineer or technical staff. “Once the crews, estimators, and office staff understood an unauthorized variance could possibly hurt or kill someone, they fell into step quickly.” Additionally, Rexroat says a detailed knowledge of fire wall/floor technology, along with other systems, goes a long way toward understanding how firestopping fits into the total fire protection package for a building.

Who carries out the firestopping?

Ken Hercenberg, a specifier for architectural firm RTKL Associates Inc., asked in an opinion column in The Construction Specifier: “Where are the certified firestoppers?” He believes there should be quantifiable qualifications for a firestopper, because without them, “Who knows who the client is getting to install these important life safety products?”

These specialty firestopping contractors—those who devote a large percentage of their time on firestopping—are winning work due to their proficiency at zero tolerance protocol, for technical expertise during interviews with A/Es, owners, code/fire officials, and the economic value overall knowledge of the firestopping trade brings to a specialty firestop contracting firm.

Standing out from the pack
FCIA worked with Factory Mutual Approvals, a division of FM Global, to develop FM 4991, Standard for the Approval of Firestop Contractors, to answer Hercenberg’s call for “approved contractors.” An International Standards Organization (ISO) -quality type of program, FM 4991 introduces a specialty firestop contracting firm to new concepts in the contracting industry. ISO writes world-renowned standards, which are used by manufacturers to monitor processes during the manufacture of products used in construction and other industries.

Firestop subcontractor quality manuals debut

Manufacturer ISO programs and FM 4991 are alike in that FM 4991 requires a quality manual be in place. Quality manuals give step-by-step descriptions of procedures a firm uses to complete firestop project, from estimate to final quality control walk-through. An FM auditor will arrive at the firestop contracting firm’s office to audit the quality manual, interviewing firm personnel to assure the contractor has the procedures in place to install firestopping with zero tolerance protocol. FM personnel also visit a project site during this audit to verify the firm is doing what it says it does.

FM 4991 acceptance

“FM 4991 has been received well by architects throughout the country,” says Aedan Gleeson of Gleeson Powers Inc. and FCIA accreditation chair. “Architects have been familiar with manufacturers’ ISO 9000 quality programs for products for years. The introduction of a quantifiable quality process for a subcontractor, run by an independent industry leader like FM, has had a big impact on acceptance”

Major firms like RTKL, Freeman White Inc., and M+O+A Architects have all begun requiring an FM 4991-approved firestop contractor in Division 7–Thermal and Moisture Protection, Section 07840–Firestopping specifications. Additionally, ARCOM MasterSpec and BSD’s SPECLink—subscription specification programs used nationally—now include FM 4991 contractors. FM 4991-approved contractors are listed on the FCIA Web site (www.fcia.org). FM personnel offer education programs at FCIA industry conferences from time to time as well. These seminars have helped contractors and management personnel prepare for the rigorous Designated Responsible Individual Exam and audit that FM Approvals conducts at the firm’s office and job site.

Independent firestop inspection

When so much time is spent on installation quality through programs like FM 4991, then why is an independent inspection agency needed to oversee firestopping installation, particularly when a professional firestopping contractor is the installer?

For a number of years, firestop industry stakeholders have been frustrated by some firms who do not take the time to install firestopping properly. “I see poor or no firestopping all the time,” says Kray Cabling Inc.’s Jess Kray, PE, in an editorial to The Electrical Distributor Magazine. “In fact, I have never seen a building that was properly firestopped throughout.” When many trades try to install firestopping, anything can happen. Some firms pay attention to the firestop installation protocol while others do not fulfill the obligations a life safety system deserves.

There are currently four methods of installation for firestopping a project:

1. A specialty firestop contractor is hired by the general contractor or owner to install the complete scope of work.

2. The general contractor/owner may split the scope of work; penetrations only and wall tops/joints/perimeter fire protection to different specialty firestop subcontractors.

3. Penetrations might be handled by the trades making the penetration, while perimeter, wall tops and joints are installed by a professional firestop specialty firm.

4. The general contractor/owner lets the trades decide how to divide the work. As a result, some trades hire specialty firestopping contractors, others handle firestopping on their own. On some projects, this decision leads to all trades installing their own firestop scope of work. Conceivably, over eight different trades could be installing firestopping on a project. This is especially true when “he who pokes it, fills it” is the method of firestopping chosen.

This latter, free-for-all method of firestop purchasing makes the scope of work difficult to manage. How can eight trades use only one manufacturer’s tested systems to firestop a building? Such cooperation is difficult, at best. Then, if eight product manufacturers are used, will inspection personnel be able to discern between products/systems during testing? Based on reports from A/Es, code/fire officials, owners, and other industry observers, this latter type of procurement method is the most difficult to control. In the event of a disaster as a result of poor firestopping, assigning responsibility can be difficult, as firms may hide behind each other to evade blame.

Firestopping is not expensive when installed properly the first time by a professional, FCIA member and/or FM 4991-Approved Firestop Contractor firm. To minimize costs, the subcontract for firestopping should be executed early in the purchasing process to better coordinate various subcontractors and optimize planning. For instance, annular space size control can save exponentially on the cost of the installed firestop system. A 25-mm (1 in.) annular space that mistakenly becomes a 51-mm (2-in.) space due lack of planning means at least three times the cost of the original system.

The case where multiple trades are responsible for firestopping work is a clear-cut example where independent inspection should be required. ASTM E 2174, Standard Practice for On-Site Inspection of Installed Fire Stops, outlines a protocol for the inspection group to follow when performing quality control on a project.

ASTM E 2174 highlights

ASTM E 2174 outlines the inspection procedure for firestop inspectors, and there are quite a few steps in the process. First, a pre-construction meeting is held with the installing contractors to review submittals, details, variances, and the inspection method to be used on the project. Next, mock-ups are built for destructive testing. Then, upon project commencement, the inspector is present to witness 10 percent of the penetration treatment on the project. A final inspection is also performed.

Destructive testing

The inspector performs destructive testing on two percent of the penetrations per 10,000 square feet of floor area, with a minimum of one for each type of penetration. Should there be a 10 percent variance to the installed firestop systems, the inspector will stop checking the project and require the contractor to re-inspect his own work. The contractor then notifies the inspector when the work is ready to be re-inspected. However, no mention is made in ASTM E 2174 as to who will pay for the extra inspections. Forms are provided in the standard for use by the inspector to assure inspection uniformity across project types and geographical locations, worldwide. These forms are submitted daily to the authorizing agency, and filed with the contractor and inspection firm.

Inspection firm qualifications

Inspection firms are hired by an authorizing agency, which could be an owner, general contractor, or code/fire official organization. Qualifications for the inspector are outlined in ASTM E 2174. For instance, the inspector should not be related to the contractor firm in any way. The inspector cannot be a competitor, supplier, owner, or other related party to the installing contractor. Another check and balance is the inspector should be experienced in this type of inspection work, with references, training records, and certifications as proof. (FCIA is currently working on an Inspector Firm Approval Program, much like FM 4991 for firestopping contractors at ASTM, with Randy Bosscawen of Multi Con Fire Containment (Columbus, Ohio) as chair. The inspector would then have quantifiable certification to review life safety firestop work.)

Inspectors can also be qualified by being acceptable to the AHJ, and through implementation of ASTM E 699, Standard Criteria for Evaluation of Agencies Involved in Testing, Quality Assurance, and Evaluating Building Components in Accordance with Test Methods Promulgated by ASTM Committee E-6, a standard for inspector firms, but not specific to firestopping.

Project close out

At the end of the project, the inspection firm performs a final close out on the project. The close-out report includes critical information for the building’s future engineering and management personnel. Included are the as-built tested system/engineering judgment documentation, any photographic records, field report forms provided from ASTM E 2174 protocol, and contact information for the installation and inspection firms. Additionally, a deviation percentage report is included, as well as information about the inspection method used during the project. Professional FCIA members and FM 4991-approved firestop contractors may already provide this documentation.

Really, why have inspection?

W. Edwards Demming, renowned management quality advisor to corporations worldwide, says design, marketing, and service testing are all tied together in a progressive cycle. The cycle, from estimate to final inspection, requires control from planning and execution through final inspection of the finished (firestopped) product. Quality monitoring assures the purchaser a process was followed to ensure a successfully assembled product or system.

Zero tolerance and engineering judgments

Firestop contractors, whether FM 4991-approved or not, need to understand the zero tolerance installation protocol governing this passive fire and life safety work. When an annular space in the field does not match up to the tested system drawing provided, the crew at the penetration must either find another tested and listed system in the documentation available, or attain an engineering judgment from the manufacturers’ technical service personnel.

Contractors need to be careful with these engineering judgments (EJs), which are also known as Equivalent Fire Resistance-Rated Assemblies (EFRRA) in FM 4991. The International Firestop Council (IFC) a firestopping manufacturer group, published a position paper on EJs discussing when they should be used. They argue that when a tested and listed system is available from any manufacturer, it should be used before an EJ is sought by the contractor. The rationale is tested and listed systems are proven performers, while an EJ is just an opinion submitted for approval by the AHJ from the manufacturer’s technical personnel or fire protection engineers. In some areas of the country, A/Es and AHJs do not allow EJs on projects, regardless of what the manufacturer or contractor thinks.

Conforming to a ‘no EJ policy’ means more research during the design stage by the architect/engineer (A/E) and at bid time for the contractor. This policy also requires the use of a specialty firestop contractor who “knows and understands the specialized knowledge required to complete this work.” The A/E and firestop contractor firm must find a firestopping manufacturer with a wide availability of tested and listed systems to complete a project without EJs. This was difficult 10 years ago, but today over 3500 tested and listed systems are found in UL’s Fire Resistance Directory, some with multiple variations, meaning many thousands of available systems. Most importantly, pre-project planning on the A/E’s part can significantly minimize or eliminate the need for EJ’s or EFRRA’s.

Zero tolerance installation means drawings should be detailed

Professional specialty Contractors performing firestop work understand the installation protocol. They have been trained by manufacturers and labor organizations, audited by FM, and have invested time and money to perform this work within zero tolerances. Unfortunately, the architectural and engineering plans are often not detailed enough to produce a quality firestopping proposal.

To really change the industry, A/Es need to give the firestopping contractor the firewalls on the mechanical systems. “It can’t be that hard for the engineer to click on his mouse, adding firewalls to the mechanical/electrical/sprinkler drawings, making a firestop ‘take-off’ much more efficient and accurate,” says Rexroat. Dennis Nolan of the Nevada Public Building Commission and speaker at the FCIA Education and Committee Action Conference seconded Rexroat’s claim. Architects argue there is not enough money to cover additional work time in their drawings because projects continue to become more competitive as fees are reduced.

FCIA has been promoting a higher level of contractor quality through education about firestopping at its conferences, work with both Factory Mutual Approvals, UL and Omega Point Laboratories,  and ASTM, and participation in industry forums, such as NFPA, the International Code Council (ICC), the Construction Specifications Institute (CSI), Specification Consultants in Independent Practice (SCIP), Society of Fire Protection Engineers (SFPE), and the American Institute of Architects (AIA). FCIA has included the architectural and code community in its seminars to promote better life safety through the specification of credible, quantifiably tested firestopping contractors.

Unfortunately, ‘trade-offs’ in the International Building Code (IBC) and NFPA 5000, NFPA Building Code, threaten the passive fire and life safety industry, and firestopping. (i.e. firewalls eliminated due to a more lenient height and area table that reduces the need for compartmentation). Manufacturers and contractors both still feel there is room for growth in firestopping, even with new code change requirements.

Additional Information

Author

Bill McHugh is the executive director of the Firestop Contractors International Association (FCIA), and the institute director for industry in CSI’s North Central Region. He delivers education programs on firestopping to all project team members and code officials nationally, and can be reached at (630) 690-0682 or via e-mail at billmchugh-jr@att.net.

MasterFormat No.

01400–Quality Requirements

07840–Firestopping

General Data–Consultants, Specialists, Services

General Data–Life Safety

General Data–Specifications

UniFormat No.

Z1020–Quality Requirements

Key words

Divisions 1, 7

ASTM International

Construction Specifications Institute

Firestop Contractors International Association

FM Approvals

International Code Council

International Firestop Council

International Standards Organization

L-rating

NFPA

Underwriters Laboratories

Abstract

In the past two years, many programs have been successfully introduced and are beginning to take hold in the firestopping industry. New developments in testing and contractor programs are helping improve life safety while providing innovation to the firestop contracting industry.

[SIDEBAR A]

For a sample firestopping specification, visit www.fcia.org/spec.07840.htm.

[PHOTO INFORMATION]

STI.jpg

Specified Technologies and other manufacturers test for perimeter fire containment systems at the labs of both Underwriters Laboratories and Omega Point Laboratories. Photo courtesy Specified Technologies Inc.

Omega.jpg

Perimeter fire containment systems are tested using the multi-story test apparatus. Photo courtesy Omega Point Laboratories.

FM logo.gif

FM Approvals, a division of FM Global, administers FM 4991, Standard for the

Approval of Firestop Contractors. Photo courtesy of FM Global.

3M Firestop.gif

Firestop products are available in many varieties to fit specific applications. Photo courtesy 3M Fire Protection Products.

Cable.jpg

Firestop pillows and putty are used for many cable penetrations. Photo courtesy Specified Technologies Inc.

Dsc00045.jpg

Firestop contractors understand life safety protocol and install fire protection ductwrap systems for grease and air ductwork. Photo courtesy Superl Inc.

FM Book.jpg

FM 4991 approved contractors are listed in the FM Directory. Photo courtesy FM Approvals.

Nelson.jpg

‘Walltop’ firestop applications, very common in corridors, are accomplished with high-production spray or sealant systems, tested and listed to UL 2079. Photo courtesy Nelson Firestop Products.

Rectorseal.jpg

Insulated piping systems are easily treated with sealant as the main active ingredient in the firestop system. Photo courtesy RectorSeal.

fryecan.tif

Prefabricated plastic pipe devices are used for many interesting firestop applications, like this 45-degree angled pipe. Photo courtesy Tremco Inc.

FCIA Logo.jpg

The FCIA’s mission is for member organizations to be recognized throughout the construction industry as preferred, quality contractors of life safety firestop systems. To that end, it created the FCIA Handbook of Accepted Firestop Knowledge (Manual of Practice).